## Slide 1
6/3/2015l Pierre Roux Air Liquide Advanced Technologies
G&C Large Helium refrigerators
Increasing Competitiveness and profit
Product Strategy & Management
THIS DOCUMENT IS CONFIDENTIAL

## Slide 2: Overview of next projects to win

## Slide 3: Overall functional analysis

## Slide 4: Overall functional analysis

## Slide 5: Functional analysis

## Slide 6: Functional analysis
Qu’est-ce qui serait selon vous standardisable ?
Que pourrait-on faire de façon plus efficace répétitive ?

## Slide 7: Equipment: : Purchase for assembling
Cryovalves
Heat Echangers
Adsorbers
Electrical Heaters
Temperature
PSV
Vacuum Vessel

## Slide 8: Equipment: Manufacturing at ALAT
Cold Box Integration
Warm Panel Integration
Insulation
Piping
Cryogenic Rotating Machines
Cold Box Integration

## Slide 9: RCB Example – JT60SA
Main HX Battery
LN2 Phase Separator
(Could be replaced by 2 Turbines)
Ads.80K
Cold HX + Ads.20K
T1
T2
T3
Overall dimensions (Ø~3m, L~12m)

## Slide 10: Possible Process to be challenged.

## Slide 11
300K -> 60K
Remove Impurities
60K -> 40K
40K -> 4,5K
~80K
~20K
Comp. HP
ORS
Regul & cond.
Compr. VLP
Interface

## Slide 12: Carnot efficiency expectation shared by our customers
Example of ESS bid : 9,1kW Eq @ 4,5K
Expected Carnot efficiency : 15,5*9,1^0,23 = 26%
Expected electrical power consumption  2,3MW
ALAT proposal : 2,6MW (23% carnot efficiency)
Michael Green published in 2008 the following curve
Nota: In all cases, there is no liquid nitrogen pre-cooling in the machines

## Slide 13: Price curve shared by our customers
Cost of Helium Refrigerators (cold boxes and compressors) versus Refrigeration at 4.5 K in 2007
Michael Green published in 2008 the following curve
For 9,1kW plant : 2,6*9,10,65= 10,5 M$ (2007)
Inflation since 2007 to 2015 : 12% -> 12 M$ ~12 M€ (2015)
To be added :test tools, capital spares, over cost due to VLP stage, control system  Total price ~ 12/0,75 ~ 16 M€

## Slide 14
COMPRESS HELIUM
LP compressors
Hot MP GHe + oil
P1
T1
Electricity
(50 or 60Hz)
Lubrication
- Required volumetric Flow
- Pressure Ratio
- Electricity frequency (50/60Hz)
Volumetric flow capacity.
Efficiency (Electrical consumption).

## Slide 15: Remove Oil From GHe
COALESCERS
Liquid Oil
GHe
+ oil vapour
GHe
+ oil dropplets
+ oil vapour
Sizing/Selection Criteria
- Required volumetric Flow
- Pressure Ratio
- Electricity frequency (50/60Hz)
Performances
Volumetric flow
Efficiency (Electrical consumption).
CHARCOAL TOWER
Ghe
+ [ H2O] = xx ppm
+ [ oil vapour] = 0
P3
T
GN2
for initial conditioning

## Slide 16: Remove Oil From GHe
To remove liquid oil from GHe
To remove oil vapor from GHe
Hot HP GHe + oil
Hot MP GHe + oil
Hot oil
HP GHe
+ oil (drops, vapor)
3-stage coalescers
Activated carbon filters
+ ORS final filters
HP GHe
+ oil (vapor)
HP GHe
Primary phase separators
1
2
3
300K HP GHe
Hot HP GHe
Hot MP GHe
To primary separate oil from gas