## DS-HX-HX-01
|  |  |  | Job nbr : | XXX |  | Document number
|  |  |  | Name : | ZZZZ
XXX-DS-YYY
PROCESS | [6 empty] | Reference
DATA |  | PLATE-FIN HEAT EXCHANGER |  |  |  |  | HX-01
Exch_Spec_HX-01.xls
| Type : | Horizontal/Vertical Aluminum brazed PFHE
[6 empty] | Run : | SLAC JLAB MAX CAPACITY 25
OPERATING CONDITIONS
Fluid |  | Units | HP_01 ~ HP_02 | N2_02c ~ N2_01 | MP_03b ~ MP_01 | LPR_03b ~ LPR_01a
Nozzle name | in
out
Fluid components |  | molar %
| Helium |  | 100 |  | 100 | 100
| Nitrogen |  |  | 100
Liquid | inlet | % | 0 | 0 | 0 | 0
fraction | outlet | % | 0 | 0 | 0 | 0
Flowrate |  | g/s | 1467.5323 | 98 | 636.2695 | 813.9328
Maximum flowrate |  | g/s
Operating | inlet | atm | 18 | 1.195 | 3.654 | 1.125
pressure | outlet | atm | 17.797 | 1.05 | 3.55 | 1.1
Operating | inlet | K | 310.0315 | 78.9132 | 78.9691 | 78.9683
temperat. | outlet | K | 81.9158 | 307.0025 | 307.0025 | 307.0025
Pressure | expected | mbar
drop | guaranteed | mbar
Duty |  | W | -1740223.2842 | 23524.1714 | 753551.0001 | 963828.8163
[6 empty] | Heat leak | -577 | W
Design pressure |  | bar g
Design temperature |  | °C
CORES CHARACTERISTICS
Exchange | type
fins | ht x thick | mm x mm
| density | FPI
Distribution | type
fins | ht x thick | mm x mm
| density | FPI
Distributors | inlet | mm
length | outlet | mm
Number of layers
Effective width |  | m
Effective length |  | m
Headers | inlet | ND
ND | outlet | ND
Nozzles | inlet | ND
ND | outlet | ND
Manifolds | inlet
ND | outlet
Cores number |  |  |  | Thickness | Parting sheets : |  |  | mm
Cores dimensions |  | Width |  |  | Side sheets : |  |  | mm
m |  | Length |  | Stacking Arrangement :
Height
Notes :
Revision | DATE | BY |  | VISA | CHECKED |  | VISA | Page

## DS-HX-HX-02
|  |  |  | Job nbr : | XXX |  | Document number
|  |  |  | Name : | ZZZZ
XXX-DS-YYY
PROCESS | [6 empty] | Reference
DATA |  | PLATE-FIN HEAT EXCHANGER |  |  |  |  | HX-02
Exch_Spec_HX-01.xls
| Type : | Horizontal/Vertical Aluminum brazed PFHE
[6 empty] | Run : | SLAC JLAB MAX CAPACITY 25
OPERATING CONDITIONS
Fluid |  | Units | HP_02 ~ HP_03a | N2_03b ~ N2_02b
Nozzle name | in
out
Fluid components |  | molar %
| Helium |  | 100
| Nitrogen |  |  | 100
Liquid | inlet | % | 0 | 100
fraction | outlet | % | 0 | 0
Flowrate |  | g/s | 1467.5323 | 84.8615
Maximum flowrate |  | g/s
Operating | inlet | atm | 17.797 | 1.2
pressure | outlet | atm | 17.794 | 1.195
Operating | inlet | K | 81.9158 | 78.946
temperat. | outlet | K | 79.746 | 78.9102
Pressure | expected | mbar
drop | guaranteed | mbar
Duty |  | W | -16665.8748 | 16675.8748
[6 empty] | Heat leak | -10 | W
Design pressure |  | bar g
Design temperature |  | °C
CORES CHARACTERISTICS
Exchange | type
fins | ht x thick | mm x mm
| density | FPI
Distribution | type
fins | ht x thick | mm x mm
| density | FPI
Distributors | inlet | mm
length | outlet | mm
Number of layers
Effective width |  | m
Effective length |  | m
Headers | inlet | ND
ND | outlet | ND
Nozzles | inlet | ND
ND | outlet | ND
Manifolds | inlet
ND | outlet
Cores number |  |  |  | Thickness | Parting sheets : |  |  | mm
Cores dimensions |  | Width |  |  | Side sheets : |  |  | mm
m |  | Length |  | Stacking Arrangement :
Height
Notes :
Revision | DATE | BY |  | VISA | CHECKED |  | VISA | Page

## DS-HX-HX-03
|  |  |  | Job nbr : | XXX |  | Document number
|  |  |  | Name : | ZZZZ
XXX-DS-YYY
PROCESS | [6 empty] | Reference
DATA |  | PLATE-FIN HEAT EXCHANGER |  |  |  |  | HX-03
Exch_Spec_HX-01.xls
| Type : | Horizontal/Vertical Aluminum brazed PFHE
[6 empty] | Run : | SLAC JLAB MAX CAPACITY 25
OPERATING CONDITIONS
Fluid |  | Units | HP_03c ~ HP_04a | MP_04a ~ MP_03a | LPR_04b ~ LPR_03a
Nozzle name | in
out
Fluid components |  | molar %
| Helium |  | 100 | 100 | 100
Liquid | inlet | % | 0 | 0 | 0
fraction | outlet | % | 0 | 0 | 0
Flowrate |  | g/s | 1467.5323 | 636.2695 | 813.9328
Maximum flowrate |  | g/s
Operating | inlet | atm | 17.702 | 3.694 | 1.138
pressure | outlet | atm | 17.642 | 3.663 | 1.131
Operating | inlet | K | 79.7532 | 55.0006 | 55.0006
temperat. | outlet | K | 56.352 | 78.9654 | 78.9654
Pressure | expected | mbar
drop | guaranteed | mbar
Duty |  | W | -180579.1923 | 79397.7334 | 101373.1197
[6 empty] | Heat leak | -171 | W
Design pressure |  | bar g
Design temperature |  | °C
CORES CHARACTERISTICS
Exchange | type
fins | ht x thick | mm x mm
| density | FPI
Distribution | type
fins | ht x thick | mm x mm
| density | FPI
Distributors | inlet | mm
length | outlet | mm
Number of layers
Effective width |  | m
Effective length |  | m
Headers | inlet | ND
ND | outlet | ND
Nozzles | inlet | ND
ND | outlet | ND
Manifolds | inlet
ND | outlet
Cores number |  |  |  | Thickness | Parting sheets : |  |  | mm
Cores dimensions |  | Width |  |  | Side sheets : |  |  | mm
m |  | Length |  | Stacking Arrangement :
Height
Notes :
Revision | DATE | BY |  | VISA | CHECKED |  | VISA | Page

## DS-HX-HX-04
|  |  |  | Job nbr : | XXX |  | Document number
|  |  |  | Name : | ZZZZ
XXX-DS-YYY
PROCESS | [6 empty] | Reference
DATA |  | PLATE-FIN HEAT EXCHANGER |  |  |  |  | HX-04
Exch_Spec_HX-01.xls
| Type : | Horizontal/Vertical Aluminum brazed PFHE
[6 empty] | Run : | SLAC JLAB MAX CAPACITY 25
OPERATING CONDITIONS
Fluid |  | Units | HP_04a ~ HP_05a | MP_05 ~ MP_04a | LPR_05 ~ LPR_04a
Nozzle name | in
out
Fluid components |  | molar %
| Helium |  | 100 | 100 | 100
Liquid | inlet | % | 0 | 0 | 0
fraction | outlet | % | 0 | 0 | 0
Flowrate |  | g/s | 1467.5323 | 636.2695 | 660.7023
Maximum flowrate |  | g/s
Operating | inlet | atm | 17.642 | 3.695 | 1.138
pressure | outlet | atm | 17.64 | 3.694 | 1.138
Operating | inlet | K | 56.352 | 52.9617 | 52.9617
temperat. | outlet | K | 54.5801 | 55.0006 | 55.0006
Pressure | expected | mbar
drop | guaranteed | mbar
Duty |  | W | -13767.0908 | 6767.3792 | 7005.0117
[6 empty] | Heat leak | -5.3 | W
Design pressure |  | bar g
Design temperature |  | °C
CORES CHARACTERISTICS
Exchange | type
fins | ht x thick | mm x mm
| density | FPI
Distribution | type
fins | ht x thick | mm x mm
| density | FPI
Distributors | inlet | mm
length | outlet | mm
Number of layers
Effective width |  | m
Effective length |  | m
Headers | inlet | ND
ND | outlet | ND
Nozzles | inlet | ND
ND | outlet | ND
Manifolds | inlet
ND | outlet
Cores number |  |  |  | Thickness | Parting sheets : |  |  | mm
Cores dimensions |  | Width |  |  | Side sheets : |  |  | mm
m |  | Length |  | Stacking Arrangement :
Height
Notes :
Revision | DATE | BY |  | VISA | CHECKED |  | VISA | Page

## DS-HX-HX-05
|  |  |  | Job nbr : | XXX |  | Document number
|  |  |  | Name : | ZZZZ
XXX-DS-YYY
PROCESS | [6 empty] | Reference
DATA |  | PLATE-FIN HEAT EXCHANGER |  |  |  |  | HX-05
Exch_Spec_HX-01.xls
| Type : | Horizontal/Vertical Aluminum brazed PFHE
[6 empty] | Run : | SLAC JLAB MAX CAPACITY 25
OPERATING CONDITIONS
Fluid |  | Units | HP-05b ~ HP_06 | 1 ~ MP_05 | LPR_06 ~ LPR_05
Nozzle name | in
out
Fluid components |  | molar %
| Helium |  | 100 | 100 | 100
Liquid | inlet | % | 0 | 0 | 0
fraction | outlet | % | 0 | 0 | 0
Flowrate |  | g/s | 1177.1523 | 636.2695 | 660.7023
Maximum flowrate |  | g/s
Operating | inlet | atm | 17.64 | 3.725 | 1.145
pressure | outlet | atm | 17.581 | 3.695 | 1.138
Operating | inlet | K | 54.5801 | 35.0162 | 35.0162
temperat. | outlet | K | 35.3671 | 52.9617 | 52.9617
Pressure | expected | mbar
drop | guaranteed | mbar
Duty |  | W | -121306.1017 | 59754.9512 | 61717.1505
[6 empty] | Heat leak | -166 | W
Design pressure |  | bar g
Design temperature |  | °C
CORES CHARACTERISTICS
Exchange | type
fins | ht x thick | mm x mm
| density | FPI
Distribution | type
fins | ht x thick | mm x mm
| density | FPI
Distributors | inlet | mm
length | outlet | mm
Number of layers
Effective width |  | m
Effective length |  | m
Headers | inlet | ND
ND | outlet | ND
Nozzles | inlet | ND
ND | outlet | ND
Manifolds | inlet
ND | outlet
Cores number |  |  |  | Thickness | Parting sheets : |  |  | mm
Cores dimensions |  | Width |  |  | Side sheets : |  |  | mm
m |  | Length |  | Stacking Arrangement :
Height
Notes :
Revision | DATE | BY |  | VISA | CHECKED |  | VISA | Page

## DS-HX-HX-06
|  |  |  | Job nbr : | XXX |  | Document number
|  |  |  | Name : | ZZZZ
XXX-DS-YYY
PROCESS | [6 empty] | Reference
DATA |  | PLATE-FIN HEAT EXCHANGER |  |  |  |  | HX-06
Exch_Spec_HX-01.xls
| Type : | Horizontal/Vertical Aluminum brazed PFHE
[6 empty] | Run : | SLAC JLAB MAX CAPACITY 25
OPERATING CONDITIONS
Fluid |  | Units | HP_06 ~ HP_07 | MP_07b ~ MP_06a | LPR_07b ~ LPR_06
Nozzle name | in
out
Fluid components |  | molar %
| Helium |  | 100 | 100 | 100
Liquid | inlet | % | 0 | 0 | 0
fraction | outlet | % | 0 | 0 | 0
Flowrate |  | g/s | 1177.1523 | 499.5 | 660.7023
Maximum flowrate |  | g/s
Operating | inlet | atm | 17.581 | 3.736 | 1.148
pressure | outlet | atm | 17.559 | 3.725 | 1.145
Operating | inlet | K | 35.3671 | 29.9975 | 29.9975
temperat. | outlet | K | 30.6693 | 35.0162 | 35.0162
Pressure | expected | mbar
drop | guaranteed | mbar
Duty |  | W | -30446.7193 | 13210.0409 | 17297.6783
[6 empty] | Heat leak | -61 | W
Design pressure |  | bar g
Design temperature |  | °C
CORES CHARACTERISTICS
Exchange | type
fins | ht x thick | mm x mm
| density | FPI
Distribution | type
fins | ht x thick | mm x mm
| density | FPI
Distributors | inlet | mm
length | outlet | mm
Number of layers
Effective width |  | m
Effective length |  | m
Headers | inlet | ND
ND | outlet | ND
Nozzles | inlet | ND
ND | outlet | ND
Manifolds | inlet
ND | outlet
Cores number |  |  |  | Thickness | Parting sheets : |  |  | mm
Cores dimensions |  | Width |  |  | Side sheets : |  |  | mm
m |  | Length |  | Stacking Arrangement :
Height
Notes :
Revision | DATE | BY |  | VISA | CHECKED |  | VISA | Page

## DS-HX-HX-07
|  |  |  | Job nbr : | XXX |  | Document number
|  |  |  | Name : | ZZZZ
XXX-DS-YYY
PROCESS | [6 empty] | Reference
DATA |  | PLATE-FIN HEAT EXCHANGER |  |  |  |  | HX-07
Exch_Spec_HX-01.xls
| Type : | Horizontal/Vertical Aluminum brazed PFHE
[6 empty] | Run : | SLAC JLAB MAX CAPACITY 25
OPERATING CONDITIONS
Fluid |  | Units | HP_07 ~ HP_08 | MP_08 ~ MP_07a | LPR_08a ~ LPR_07a
Nozzle name | in
out
Fluid components |  | molar %
| Helium |  | 100 | 100 | 100
Liquid | inlet | % | 0 | 0 | 0
fraction | outlet | % | 0 | 0 | 0
Flowrate |  | g/s | 1177.1523 | 499.5 | 450.7023
Maximum flowrate |  | g/s
Operating | inlet | atm | 17.559 | 3.74 | 1.149
pressure | outlet | atm | 17.551 | 3.736 | 1.148
Operating | inlet | K | 30.6693 | 24.1849 | 24.1849
temperat. | outlet | K | 26.2701 | 29.9975 | 29.9975
Pressure | expected | mbar
drop | guaranteed | mbar
Duty |  | W | -29083.3175 | 15408.2889 | 13697.0286
[6 empty] | Heat leak | -22 | W
Design pressure |  | bar g
Design temperature |  | °C
CORES CHARACTERISTICS
Exchange | type
fins | ht x thick | mm x mm
| density | FPI
Distribution | type
fins | ht x thick | mm x mm
| density | FPI
Distributors | inlet | mm
length | outlet | mm
Number of layers
Effective width |  | m
Effective length |  | m
Headers | inlet | ND
ND | outlet | ND
Nozzles | inlet | ND
ND | outlet | ND
Manifolds | inlet
ND | outlet
Cores number |  |  |  | Thickness | Parting sheets : |  |  | mm
Cores dimensions |  | Width |  |  | Side sheets : |  |  | mm
m |  | Length |  | Stacking Arrangement :
Height
Notes :
Revision | DATE | BY |  | VISA | CHECKED |  | VISA | Page

## DS-HX-HX-08
|  |  |  | Job nbr : | XXX |  | Document number
|  |  |  | Name : | ZZZZ
XXX-DS-YYY
PROCESS | [6 empty] | Reference
DATA |  | PLATE-FIN HEAT EXCHANGER |  |  |  |  | HX-08
Exch_Spec_HX-01.xls
| Type : | Horizontal/Vertical Aluminum brazed PFHE
[6 empty] | Run : | SLAC JLAB MAX CAPACITY 25
OPERATING CONDITIONS
Fluid |  | Units | HP_09_b ~ HP_09a | T2_10b ~ MP_08 | LPR_09 ~ LPR_08a
Nozzle name | in
out
Fluid components |  | molar %
| Helium |  | 100 | 100 | 100
Liquid | inlet | % | 0 | 0 | 0
fraction | outlet | % | 0 | 0 | 0
Flowrate |  | g/s | 677.1323 | 499.5 | 450.7023
Maximum flowrate |  | g/s
Operating | inlet | atm | 17.551 | 3.751 | 1.152
pressure | outlet | atm | 17.53 | 3.74 | 1.149
Operating | inlet | K | 26.2701 | 16.65 | 16.65
temperat. | outlet | K | 16.8136 | 24.1849 | 24.1849
Pressure | expected | mbar
drop | guaranteed | mbar
Duty |  | W | -38143.3653 | 20344.1018 | 17858.2635
[6 empty] | Heat leak | -59 | W
Design pressure |  | bar g
Design temperature |  | °C
CORES CHARACTERISTICS
Exchange | type
fins | ht x thick | mm x mm
| density | FPI
Distribution | type
fins | ht x thick | mm x mm
| density | FPI
Distributors | inlet | mm
length | outlet | mm
Number of layers
Effective width |  | m
Effective length |  | m
Headers | inlet | ND
ND | outlet | ND
Nozzles | inlet | ND
ND | outlet | ND
Manifolds | inlet
ND | outlet
Cores number |  |  |  | Thickness | Parting sheets : |  |  | mm
Cores dimensions |  | Width |  |  | Side sheets : |  |  | mm
m |  | Length |  | Stacking Arrangement :
Height
Notes :
Revision | DATE | BY |  | VISA | CHECKED |  | VISA | Page

## DS-HX-HX-09
|  |  |  | Job nbr : | XXX |  | Document number
|  |  |  | Name : | ZZZZ
XXX-DS-YYY
PROCESS | [6 empty] | Reference
DATA |  | PLATE-FIN HEAT EXCHANGER |  |  |  |  | HX-09
Exch_Spec_HX-01.xls
| Type : | Horizontal/Vertical Aluminum brazed PFHE
[6 empty] | Run : | SLAC JLAB MAX CAPACITY 25
OPERATING CONDITIONS
Fluid |  | Units | HP_09a ~ HP_10a | LPR_10 ~ LPR_09
Nozzle name | in
out
Fluid components |  | molar %
| Helium |  | 100 | 100
Liquid | inlet | % | 0 | 0
fraction | outlet | % | 0 | 0
Flowrate |  | g/s | 677.1323 | 450.7023
Maximum flowrate |  | g/s
Operating | inlet | atm | 17.53 | 1.152
pressure | outlet | atm | 17.53 | 1.152
Operating | inlet | K | 16.8136 | 16.5858
temperat. | outlet | K | 16.7793 | 16.65
Pressure | expected | mbar
drop | guaranteed | mbar
Duty |  | W | -148.0058 | 153.0058
[6 empty] | Heat leak | -5 | W
Design pressure |  | bar g
Design temperature |  | °C
CORES CHARACTERISTICS
Exchange | type
fins | ht x thick | mm x mm
| density | FPI
Distribution | type
fins | ht x thick | mm x mm
| density | FPI
Distributors | inlet | mm
length | outlet | mm
Number of layers
Effective width |  | m
Effective length |  | m
Headers | inlet | ND
ND | outlet | ND
Nozzles | inlet | ND
ND | outlet | ND
Manifolds | inlet
ND | outlet
Cores number |  |  |  | Thickness | Parting sheets : |  |  | mm
Cores dimensions |  | Width |  |  | Side sheets : |  |  | mm
m |  | Length |  | Stacking Arrangement :
Height
Notes :
Revision | DATE | BY |  | VISA | CHECKED |  | VISA | Page

## DS-HX-HX-10
|  |  |  | Job nbr : | XXX |  | Document number
|  |  |  | Name : | ZZZZ
XXX-DS-YYY
PROCESS | [6 empty] | Reference
DATA |  | PLATE-FIN HEAT EXCHANGER |  |  |  |  | HX-10
Exch_Spec_HX-01.xls
| Type : | Horizontal/Vertical Aluminum brazed PFHE
[6 empty] | Run : | SLAC JLAB MAX CAPACITY 25
OPERATING CONDITIONS
Fluid |  | Units | HP_10c ~ HP_11 | LPR_11b ~ LPR_10
Nozzle name | in
out
Fluid components |  | molar %
| Helium |  | 100 | 100
Liquid | inlet | % | 0 | 0
fraction | outlet | % | 0 | 0
Flowrate |  | g/s | 362.8123 | 450.7023
Maximum flowrate |  | g/s
Operating | inlet | atm | 17.515 | 1.156
pressure | outlet | atm | 17.482 | 1.152
Operating | inlet | K | 16.7794 | 7.6441
temperat. | outlet | K | 7.7451 | 16.5858
Pressure | expected | mbar
drop | guaranteed | mbar
Duty |  | W | -21712.1012 | 21807.1012
[6 empty] | Heat leak | -95 | W
Design pressure |  | bar g
Design temperature |  | °C
CORES CHARACTERISTICS
Exchange | type
fins | ht x thick | mm x mm
| density | FPI
Distribution | type
fins | ht x thick | mm x mm
| density | FPI
Distributors | inlet | mm
length | outlet | mm
Number of layers
Effective width |  | m
Effective length |  | m
Headers | inlet | ND
ND | outlet | ND
Nozzles | inlet | ND
ND | outlet | ND
Manifolds | inlet
ND | outlet
Cores number |  |  |  | Thickness | Parting sheets : |  |  | mm
Cores dimensions |  | Width |  |  | Side sheets : |  |  | mm
m |  | Length |  | Stacking Arrangement :
Height
Notes :
Revision | DATE | BY |  | VISA | CHECKED |  | VISA | Page

## DS-HX-HX-12
|  |  |  | Job nbr : | XXX |  | Document number
|  |  |  | Name : | ZZZZ
XXX-DS-YYY
PROCESS | [6 empty] | Reference
DATA |  | PLATE-FIN HEAT EXCHANGER |  |  |  |  | HX-12
Exch_Spec_HX-01.xls
| Type : | Horizontal/Vertical Aluminum brazed PFHE
[6 empty] | Run : | SLAC JLAB MAX CAPACITY 25
OPERATING CONDITIONS
Fluid |  | Units | HP_11 ~ T4_13a | LPR_13 ~ LPR_12a
Nozzle name | in
out
Fluid components |  | molar %
| Helium |  | 100 | 100
Liquid | inlet | % | 0 | 0
fraction | outlet | % | 0 | 0
Flowrate |  | g/s | 362.8123 | 93.8585
Maximum flowrate |  | g/s
Operating | inlet | atm | 17.482 | 1.156
pressure | outlet | atm | 17.48 | 1.156
Operating | inlet | K | 7.7451 | 5.4105
temperat. | outlet | K | 7.0038 | 7.7387
Pressure | expected | mbar
drop | guaranteed | mbar
Duty |  | W | -1311.733 | 1316.733
[6 empty] | Heat leak | -5 | W
Design pressure |  | bar g
Design temperature |  | °C
CORES CHARACTERISTICS
Exchange | type
fins | ht x thick | mm x mm
| density | FPI
Distribution | type
fins | ht x thick | mm x mm
| density | FPI
Distributors | inlet | mm
length | outlet | mm
Number of layers
Effective width |  | m
Effective length |  | m
Headers | inlet | ND
ND | outlet | ND
Nozzles | inlet | ND
ND | outlet | ND
Manifolds | inlet
ND | outlet
Cores number |  |  |  | Thickness | Parting sheets : |  |  | mm
Cores dimensions |  | Width |  |  | Side sheets : |  |  | mm
m |  | Length |  | Stacking Arrangement :
Height
Notes :
Revision | DATE | BY |  | VISA | CHECKED |  | VISA | Page

## DS-HX-HX-13
|  |  |  | Job nbr : | XXX |  | Document number
|  |  |  | Name : | ZZZZ
XXX-DS-YYY
PROCESS | [6 empty] | Reference
DATA |  | PLATE-FIN HEAT EXCHANGER |  |  |  |  | HX-13
Exch_Spec_HX-01.xls
| Type : | Horizontal/Vertical Aluminum brazed PFHE
[6 empty] | Run : | SLAC JLAB MAX CAPACITY 25
OPERATING CONDITIONS
Fluid |  | Units | T4_13d ~ HP_SCa | LPR_14 ~ LPR_13
Nozzle name | in
out
Fluid components |  | molar %
| Helium |  | 100 | 100
Liquid | inlet | % | 0 | 0.19317
fraction | outlet | % | 0 | 0
Flowrate |  | g/s | 319.6085 | 93.8585
Maximum flowrate |  | g/s
Operating | inlet | atm | 3.301 | 1.156
pressure | outlet | atm | 3.3 | 1.156
Operating | inlet | K | 5.5113 | 4.3818
temperat. | outlet | K | 5.3045 | 5.4105
Pressure | expected | mbar
drop | guaranteed | mbar
Duty |  | W | -745.6985 | 750.6985
[6 empty] | Heat leak | -5 | W
Design pressure |  | bar g
Design temperature |  | °C
CORES CHARACTERISTICS
Exchange | type
fins | ht x thick | mm x mm
| density | FPI
Distribution | type
fins | ht x thick | mm x mm
| density | FPI
Distributors | inlet | mm
length | outlet | mm
Number of layers
Effective width |  | m
Effective length |  | m
Headers | inlet | ND
ND | outlet | ND
Nozzles | inlet | ND
ND | outlet | ND
Manifolds | inlet
ND | outlet
Cores number |  |  |  | Thickness | Parting sheets : |  |  | mm
Cores dimensions |  | Width |  |  | Side sheets : |  |  | mm
m |  | Length |  | Stacking Arrangement :
Height
Notes :
Revision | DATE | BY |  | VISA | CHECKED |  | VISA | Page