{"text_format":"1","workbook":"xlsx","n_sheets":2,"sheets":["lignes","Piping_class"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":5,"comments":1,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"lignes","index":0,"n_rows":6,"n_cols":27,"rows_kept":6,"cut":false,"hidden":false,"merged":[]}
[]
[null,"Norm","EN"]
[null,"Piping Class","HP"]
[]
[null,"Type","Tag","Description","Fluid","Fluid n°","Pin\n[bar a]","T\n[K]","mass flow\n[g/s]","Vapor VOLUME fraction","density (ρ)\n[kg/m3]",{"$f":"IF(C2=\"EN\",\"DN\",IF(C2=\"ASME\",\"NPS [inch]\",\"\"))","v":"DN"},"Piping class","f int\n[mm]","Ra\n[µm]","Speed V\n[m/s]","Vsound\n[m/s]","Mach Number","Re","ρv²\n(Pa)","l","dP linear\n[mbar/m]","dP singular\n[mbar/elb]","Length\n[m]","Elbows","dP\n[mbar]","dP total\n[mbar]"]
[null,"Pipe","PI-1200","From ORS to warm panel","Water",{"$f":"Fluidnb(E6)","v":27},3,300,100,1,{"$f":"rho_vol(F6,G6,H6,J6)","v":996.64374900896462},25,"HP",{"$f":"Dint(_Norm,M6,L6)","v":30.500000000000004},50,{"$f":"4*1000*I6/(K6*PI()*N6^2)","v":0.137331604065938},{"$f":"Soundspeed(F6,G6,H6,J6)","v":1500.9515113093221},{"$f":"P6/Q6","v":9.1496362827963576E-5},{"$f":"Re_(F6,I6,G6,H6,K6,N6)","v":{"$error":"#VALUE!"}},{"$f":"K6*P6^2","v":18.796670684081107},{"$f":"Colebrook(N6,O6,S6)","v":{"$error":"#VALUE!"}},{"$f":"dP_linear(F6,I6,G6,H6,K6,N6,O6)","v":{"$error":"#VALUE!"}},{"$f":"dP_elb(I6,K6,N6)","v":2.8195006027733394E-2},50,8,{"$f":"V6*X6+W6*Y6","v":{"$error":"#VALUE!"}}]

{"sheet":"Piping_class","index":1,"n_rows":65,"n_cols":11,"rows_kept":65,"cut":false,"hidden":false,"merged":[]}
[]
[null,null,null,null,null,"Outlet Diameter [mm]",null,"Thickness [mm]"]
[null,"Nominal Diameter","DN","NPS",null,"EN","ASME","27 bar EN","10 bar EN","27 bar ASME","10 bar ASME"]
[null,{"$f":"IF(_Norm=\"EN\",C4,IF(_Norm=\"ASME\",D4,\"-\"))","v":8},8,"1/4\"",null,{"$f":"Dext(F$3,$B4)","v":13.5},{"$f":"Dext(G$3,$B4)","v":13.7},{"$f":"Thck(\"EN\",\"HP\",$C4)","v":1.6},{"$f":"Thck(\"EN\",\"LP\",$C4)","v":1.6},{"$f":"Thck(\"ASME\",\"HP\",$D4)","v":1.65},{"$f":"Thck(\"ASME\",\"LP\",$D4)","v":1.65}]
[null,10,10,"3/8\"",null,{"$f":"Dext(F$3,$B5)","v":17.2},17.100000000000001,{"$f":"Thck(\"EN\",\"HP\",$C5)","v":1.6},{"$f":"Thck(\"EN\",\"LP\",$C5)","v":1.6},{"$f":"Thck(\"ASME\",\"HP\",$D5)","v":1.65},{"$f":"Thck(\"ASME\",\"LP\",$D5)","v":1.65}]
[null,15,15,"1/2\"",null,21.3,21.3,1.6,1.6,1.65,1.65]
[null,20,20,"3/4\"",null,26.9,26.7,1.6,1.6,1.65,1.65]
[null,25,25,"1\"",null,33.700000000000003,33.4,1.6,1.6,1.65,1.65]
[null,32,32,"1\"1/4",null,42.4,42.2,1.6,1.6,1.65,1.65]
[null,40,40,"1\"1/2",null,48.3,48.3,1.6,1.6,1.65,1.65]
[null,50,50,"2\"",null,60.3,60.3,1.6,1.6,2.77,1.65]
[null,65,65,"2\"1/2",null,76.099999999999994,73,1.6,1.6,3.05,1.65]
[null,80,80,"3\"",null,88.9,88.9,2,2,3.05,2.11]
[null,100,100,"4\"",null,114.3,114.3,2,2,3.05,2.11]
[null,125,125,"5\"",null,139.69999999999999,141.30000000000001,2,2,3.4,2.77]
[null,150,150,"6\"",null,168.3,168.3,2.2999999999999998,2,3.4,2.77]
[null,200,200,"8\"",null,219.1,219.1,2.9,2.6,3.76,3.76]
[null,250,250,"10\"",null,273,273,3.6,2.9,9.27,4.1900000000000004]
[null,300,300,"12\"",null,323.89999999999998,323.89999999999998,4.5,3.6,9.5299999999999994,4.57]
[null,350,350,"14\"",null,355.6,355.6,5,4,9.5299999999999994,4.7699999999999996]
[null,400,400,"16\"",null,406.4,406.4,5.6,4.5,9.5299999999999994,4.7699999999999996]
[null,450,450,"18\"",null,457.2,457.2,{"$error":"#VALUE!"},5,9.5299999999999994,4.7699999999999996]
[null,500,500,"20\"",null,508,508,{"$error":"#VALUE!"},5.6,{"$error":"#VALUE!"},5.54]
[null,600,600,"24\"",null,610,609.6,{"$error":"#VALUE!"},6.3,{"$error":"#VALUE!"},9.5299999999999994]
[null,700,700,"28\"",null,711,711.2,{"$error":"#VALUE!"},8,{"$error":"#VALUE!"},9.5299999999999994]
[]
[null,"Raccourci","Fluid","Fluid n°","Ordre"]
[null,"He","Helium",11,1,"Seuls les fluides en bleu sont codés"]
[null,"N2","Nitrogen 73",21,2]
[null,"H2","Hydrogen, Equilibrium",12,3]
[null,"Water","Water",27,4]
[null,"O2","Oxygen 85",25,5]
[null,"CH4","Methane 89",19,6]
[null,"CO","Carbon Monoxide",6,7]
[null,"CO2","Carbon Dioxide",5,8]
[null,"NH3","Ammonia",1,9]
[null,"Ar","Argon",2,10]
[null,"C3H8","Propane",26,11]
[null,"C4H10","Butane, Iso",3,12]
[null,"Xe","Xenon",28,13]
[null,"Ne","Neon 91",20,14]
[null,"Kr","Krypton",17,15]
[null,null,"Butane, Normal",4]
[null,"De","Deuterium",7]
[null,"Ethane","Ethane",8]
[null,null,"Ethylene 81",9]
[null,"Ethylene","Ethylene 86",10]
[null,null,"Hydrogen, Normal",13]
[null,null,"Hydrogen, Ortho",14]
[null,null,"Hydrogen, Para",15]
[null,"H2S","Hydrogen Sulfide",16]
[null,null,"Methane 86",18]
[null,null,"Nitrogen 86",22]
[null,null,"Nitrogen Trifluoride",23]
[null,null,"Oxygen 78",24]
[null,null,"R-11",29]
[null,null,"R-12",30]
[null,null,"R-22",31]
[null,null,"R-32",32]
[null,null,"R-123",33]
[null,null,"R-124",34]
[null,null,"R-125",35]
[null,null,"R-134a 92",36]
[null,null,"R-134a 93",37]
[null,null,"R-152a",38]